## Slide 1: ICDE reference list: Overview Website: https://projectportal.afconsult.com/ProjectPortal/icde
List of references including a short description of the ICDE report
Summary report
    ICDE Project Report: Summary of Phase VIII of the International Common-Cause Data Exchange Project ; NEA/CSNI/R(2023)9, Replacing NEA/CSNI/R(2019)3
  Technical Notes
    General Coding Guidelines, Issue 5, 2026
    ICDE Quality Assurance Programme, ICDEPR05, Rev. 2, 2017
  Component reports for:
    Centrifugal Pumps, Diesel Generators, Motor-Operated Valves, Safety Relief Valves, Check Valves, Batteries, Level Measurement, Breakers Control Rod Drive Assemblies, Heat Exchangers
  Topical analysis reports, 7 Published, 1 Final manuscript, 3 in preparation

## Slide 2: ICDE Event General Coding Guidelines
Common Cause Event: A dependent failure in which two or more component fault states exist simultaneously, or within a short time interval, and are a direct result of a shared cause
In the context of the data collection part of the ICDE project, complete as well as potential CCF events will be collected. To include all events of interest, an “ICDE event” is defined as follows:
ICDE Event: Impairment1) of two or more components (with respect to performing a specific function) that exists over a relevant time interval 2) and is the direct result of a shared cause.
Possible attributes of impairment are:
complete failure of the component to perform its function
degraded ability of the component to perform its function
incipient failure of the component
default: component is working according to specification
Relevant time interval: two pertinent inspection periods (for the particular impairment) or, if unknown, a scheduled outage period.
The so called "complete CCF events" are of particular interest. A "complete CCF event" is defined as a dependent failure of all components of an exposed population where the fault state of each of its components is "complete failure to perform its function" and where these fault states exist simultaneously and are the direct result of a shared cause.
“Partial CCF” is also of interest and is defined as complete failure of at least two components, but not all of the exposed population, where these fault states exist simultaneously and are the direct result of a shared cause.
The ICDE data analysts may add interesting events that fall outside the ICDE event definition but are examples of recurrent - eventually non random - failures.
From C8: Component impairment vector: If parts were replaced on some components due to failures of parallel components, the Incipient code is used for the components that didn’t actually experience a failure. This also applies if it was decided to implement said replacement at a later time.

## Slide 3: ICDE reference list, https://www.oecd-nea.org/nsd/docs/indexcsni.html
Summary reports
ICDE Project Report: Summary of Phase VII of the International Common-Cause Data Exchange Project NEA/CSNI/R(2019)3, June 2019.
ICDE Project Report: Summary of Phase VIII of the International Common-Cause Data Exchange Project NEA/CSNI/R(2023)9, June 2025.
  Replacing NEA/CSNI/R(2019)3
Technical Note
ICDE Project General Coding Guidelines,
  On https://projectportal.afconsult.com/ProjectPortal/icde
  Public Issue 5 20260518
ICDE Quality Assurance Programme, ICDEPR05, Rev. 2, 2017
Component reports
Collection and analysis of common-cause failure of centrifugal pumps [NEA/CSNI/R(2013)2], June 2013.
  [Replacing NEA/CSNI/R(99)2]
Lessons Learnt from Common-Cause Failure of Emergency Diesel Generators in Nuclear Power Plants – A Report from the International Common-Cause Failure Data Exchange (ICDE) Project [NEA/CSNI/R(2018)5], September 2018.
  [Replacing NEA/CSNI/R(2000)20],
Collection and analysis of common-cause failure of check valves [NEA/CSNI/R(2003)15], February 2003Collection and analysis of common-cause failure of switching devices and circuit breakers [NEA/CSNI/R(2008)01], October 2007.
Collection and analysis of common-cause failure of level measurement components [NEA/CSNI/R(2008)8, July 2008.
Collection and analysis of common-cause failure of control rod drive assemblies [NEA/CSNI/R(2013)4], June 2013.
Collection and analysis of common-cause failure of heat exchangers [NEA/CSNI/R(2015)11], April 2013.
ICDE project: Common-Cause Failures of Safety and Relief Valves [NEA/CSNI/R(2020)17] March 2024, Published
[Replacing NEA/CSNI/R(2002)19],
ICDE Report: Lessons Learned from Common-Cause Failures of Motor-Operated Valves [NEA/CSNI/R(2021)7] 2022 PRG approved 2021
  [Replacing NEA/CSNI/R(2001)10],
Final Manuscript available
Collection and analysis of common-cause failure of batteries. [NEA/CSNI/R(2023)8], 20XX. PRG Approved 2022
  [Replacing NEA/CSNI/R(2003)19],

## Slide 4: Scope of Topical analysis
Aim of the topical reports is to capture insights for possible improvements and defences for the topic in question.
The topical analysis is mainly intended for designers, operators and regulators
to improve their understanding on CCF events and
to give insights of relevant failure mechanisms
to enlarge their understanding on reducing CCF risks
to give valuable experience to support and improve the modelling in probabilistic risk assessment (PRA) models
Published at OECD/NEA
Diesels all affected (143 events)
Plant Modifications (53 events)
Improving Testing (59 events)
Multi-unit events (87 multi-unit events)
Inter-system dependencies (25 intersystem events)
External Environmental Factors (64 events)
Pre initiator HFE (51 complete CCF events)
Final Manuscript available
Safety Culture Deficiencies in CCF Events (first draft) (144 events)
Under development 2026
Guidance and data interpretation (complete draft 2026)
Ageing (first draft fall 2025, third workshop fall 2026)
I&C (first workshop spring 2026)

## Slide 5: Short description of the ICDE topical reports

## Slide 6: External Environmental Factors
An external factor event is a CCF event or CCF fragility (impairment) related to external or environmental factors or an event directly caused or triggered by such factors (e.g., weather or environmental conditions). (64 events)
Provide insights into the type of external factor events in the ICDE database.
Gives valuable experience to support and improve the external event modelling in probabilistic risk assessment (PRA) models and provide with CCF data for quantification purposes.
Assessment of the event parameters: event cause, coupling factor, corrective action, CCF root cause, event severity and detection method.
The major observed event cause is “Abnormal environmental stress” (42%) and it is relatively over-represented with a factor of 9 compared to the complete ICDE database.
For about 31% of the events, the concluded CCF root cause was solely or predominant design, (Deficiencies in the design of components or systems), where foreseen environmental aspects significantly contributed.
An equally large share of the events was determined to be “Environmental trigger” events, i.e., events with a non-foreseen environmental cause.
The engineering analysis addressed the “cause” or “trigger” of the external factor event, expressed by different hazard groups and classification of their causes and areas of improvement to prevent the events from happening again.

## Slide 7: Diesel events Affecting Entire Exposed Population
The scope of “Diesels all affected” topic was to identify failure mechanisms that are able to impact all diesels in an exposed population, so called “all affected” diesel failures (142 events)
All diesels in an exposed population either failed or were degraded or showed an incipient impairment due the same cause
Aims to get broader insights in failure mechanisms that are potentially able to lead to complete common cause failures of emergency diesel generators.
Areas of improvement to prevent the event for happening again
Design of system or site
Design of component - 28%
Surveillance of component
Maintenance or testing of component - 34%
Operation of component
Management system of plant (QA of vendor, spare parts management, training of personnel, sufficient resources/staff etc.) - 16%

## Slide 8: CCFs due to Plant Modifications
Evaluates CCF events that occurred due to modifications, backfitting, and/or replacements (53 events)
The share of complete CCFs (22%) is significantly larger than the share of complete CCFs in the whole database, which is only about 10%
For the severe events (complete or partial CCF), I&C modifications were most common.
Several problems relate to modified protection devices of the main components (e.g. protection relays, contacts and wiring).
No CCF events identified that were related to modifications resulting from a regulatory backfit, i.e., relating to new or amended regulatory requirements or regulations
Modifications have the potential to cause CCFs, especially CCF which affect all redundant components at once
A stringent assessment of possible interactions on system-level
A comprehensive post-modification testing program should be developed and implemented
Modifications of settings, testing procedures and maintenance procedures (e.g. change of lubrication, grease etc.) should be comprehensively tested after the modification.
If possible, modifications in redundant trains should not be implemented simultaneously
Modifications to I&C systems and protection devices should be performed with special care
CCFs due to the modification of sub components are mostly related to the design of the sub-component itself and can be prevented by the owner by a thorough design evaluation and a profound review of the manufacturers.

## Slide 9: Provision against CCFs by Improving Testing
The main objective was to study CCF events, where fault states or impairments could not be detected (59 events)
  in normal recurrent tests because the scope of tests was insufficient or
  no appropriate tests existed
Enlarge the understanding on reducing CCF risks by improving testing and to give insights of relevant failure mechanisms.
Inadequacies in testing have been observed in all investigated aspects of testing, which are: extent of test, QA of test, performing the test and verification of operability.
  The most common component types were Emergency Diesel Generators, Centrifugal pumps and Safety relief valves. Level measurements contribute with several severe events.
  The most common CCF root cause was procedure deficiencies (58%).
  The most common area to find test inadequacies is in QA of testing.
  No event was identified to be caused by inadequate test intervals.

## Slide 10: Multi-Unit CCF Events
The main goal was to study CCF events that occurred at multiple units at the same site to give insights of relevant failure mechanisms. (87 multi-unit events)
The observed multi-unit events were classified as: Internal factors (shared design or organizational factor), External factors (physical, external or environmental connection), or Fleet CCF events (same or similar events occurring at multiple sites).
The analysis included an assessment of the event parameters; event cause, coupling factor, detection method, corrective action, CCF root cause and multi-unit event severity
Multi-unit events were observed for a wide range of component types. Emergency diesel generators and Centrifugal pumps accounted for more than 50% of the events.
The most common CCF root cause (nearly 60%) for multi-unit CCF events was deficiency in the design of components and systems. Hence design is significantly overrepresented compared to the total observed CCF event population.
Events with observed environmental deficiencies were caused by harsh environmental conditions, such as severe weather or abnormal debris in a raw water source which usually require design improvements to prevent reoccurrence.
About 10% of the events were complete multi-unit CCF events.

## Slide 11: Inter-system dependencies
The goal was to analyze events were a single CCF failure mechanism affects multiple systems
  Events where a single CCF failure mechanism affected components in more than one different system or affected more than one different safety function
  The topical report includes 25 intersystem events, involving a total of 33 ICDE events affecting more than one different system (or safety function).
For classification of intersystem dependency events, two parameters were considered; the degree of failure and degree of simultaneity-
  By combining these, the following classification was concluded:
    Actual intersystem dependency
    Partial/Incipient intersystem dependency
    Potential intersystem dependency
    Inter-CCCG dependency
Intersystem CCFs are rare events (the 25 events correspond to about 1.4% of all CCF events in the ICDE database and about 1.9% of the complete CCFs, i.e. ~0.02 in an intersystem β-factor model), yet their existence and their risk significance should not be overlooked.
Modification of component protection devices (overcurrent, torque etc.) should be performed with great care.
Maintenance or modification activities in one system resulting in a CCF in another system were observed.
Diversity on the component level does not ensure diversity on piece part level in different systems. For example, the same type of breaker is used in multiple systems and is vulnerable to a CCF mechanism.
Intersystem dependencies could exist on a lower component level which is normally not considered in PRA.
Due to its risk significance intersystem dependencies should be taken into account accordingly when performing a PRA, while also considering the rarity of these events and credit for defences that could prevent or mitigate their occurrence.

## Slide 12: Pre initiator Human Failure Events
The goal was to analyze event that is caused by inappropriate actions or human inactions, such as misalignments and miscalibrations (51 events)
  All the included events were complete CCFs.
  The event set also includes important Intersystem HFEs and Multi-unit HFEs.
The engineering analysis addressed:
  The involved act that determines the “cause” or “trigger” of the human failure event.
    corrective or preventive maintenance (e.g., improper installation), modification or replacement, surveillance testing, operation and other/unknown actions
  The performance shaping factors (PSFs) that impact the pre-initiator HFEs.
    written work plans, procedures, training, complexity and number of steps, reliance on memory, ergonomics, and the task environment
  The latency of the event until failure or detection of degraded component state
Deficiency in the procedure was the main CCF root cause for the complete common-cause pre-initiator HFEs (74%).
The most common acts were corrective/preventive maintenance followed by surveillance testing.
The most common type of PSF was procedures, followed by training and written work plans.
About 55% of the events had high latency, including several latent events only detected by demand.
The most common plant state was outage followed by at power.
About 18% of the HFEs were marked as safety culture issues.
The pre-initiator HFEs from the ICDE database provides valuable insights into dependencies since many of these dependencies are not typically modelled in a HRA.

## Slide 13: Topical report in preparation – Safety culture Events
Analysis of Safety Culture Deficiencies in Common-Cause Failure Events (144 events)
The purpose of this topical report is to study ICDE events with safety culture deficiencies, their significance, and their impact on safety.
The specific objectives of this topical report are
  To identify and apply the coding of the Safety Culture Model (SCM) attributes.
  To assess the degree of certainty of these attributes in the event assessment.
  To provide valuable insights and recommendations of contributing areas of the safety culture that results in a CCF event.
  To present the most important findings and lessons learned and make these available to the broader nuclear safety and risk communities.

## Slide 14: Topical report in preparation – Draft: Quantification guidance and data interpretation
Quantification guidance and data interpretation in component-specific quantitative applications
  Quantitative applications of various component types are a possible way to demonstrate the applicability of the collected ICDE data for quantification.
  From the quantitative applications there are several findings needing to be addressed and resolved. This report aims to explore and resolve those issues and demonstrate the use of the ICDE data.

## Slide 15: Topical report in preparation – To be drafted
Ageing (first draft fall 2025, third workshop fall 2026)
I&C (first workshop spring 2026)

## Slide 17: ICDE reference list, https://www.oecd-nea.org/nsd/docs/indexcsni.html
ICDE Topical reports, Published at OECD/NEA
Proceedings of ICDE Workshop on the qualitative and quantitative use of ICDE Data [NEA/CSNI/R(2001)8, November 2002.
ICDE Workshop - Collection and Analysis of Emergency Diesel Generator Common-Cause Failures Impacting Entire Exposed Population [NEA/CSNI/R(2017)8], August 2017.
ICDE Topical report: Collection and Analysis of Common-Cause Failures due to Plant Modifications NEA/CSNI/R(2019)4, March 2020.
ICDE Topical report: Provision against Common-Cause Failures by Improving Testing NEA/CSNI/R(2019)5, November 2022
ICDE Topical report: Collection and Analysis of Multi-Unit Common-Cause Failure Events NEA/CSNI/R(2019)6, November 2022
ICDE Topical report: Intersystem dependencies NEA/CSNI/R(2020)1, May 2022.
ICDE Topical reports, Published at OECD/NEA
ICDE project: Operational Experience on Common-Cause Failures due to External Environmental Factors, NEA/CSNI/R(2020/15 R
  [Replacing NEA/CSNI/R(2015)17],
ICDE Topical Report: Collection and Analysis of Common Cause Pre-Initiator Human Failure Events NEA/CSNI/R(2022)1

## Slide 18: Recent final manuscripts to be published
The reports are available on member-only access area on the ICDE portal project until these reports are officially published.
Summary report
ICDE Project Report: Summary of Phase VIII of the International Common-Cause Data Exchange Project NEA/CSNI/R(2023)9, 2025. Published
Component reports
NEA/CSNI/R (2020)17 ICDE Project report: Common-Cause Failures of Safety and Relief valves, Published
NEA/CSNI/R(2021)7 ICDE Project report: Lessons Learned from common cause failures of Motor-operated Valves Published
Collection and analysis of common-cause failure of batteries [NEA/CSNI/R(2023)8], 20XX. PRG Approved 2022 Copyright OK
Topical reports
NEA/CSNI/R(2020)15 ICDE Topical Report: Operational experience on common-cause failures due to External Environmental Factors Published
NEA/CSNI/R(2022)1 ICDE Topical report: Collection and Analysis of Common-Cause Pre-initiator Human Failure Events Published